## Table 1 (2)
Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Column10 | Column11 | Column12
Detailed Performance Summary For R-134a_Qx_100to20_dTe_const_Tc_41to20C Project: 30XW_China 07.20.2026 Prepared By: Mikhail Terekhov 03:47
Load Line
Unit Performance | ** | *** | [7 empty] | -1
User-specified Cooling Capacity, kW |  | 1000 | 900 | 800 | 700 | 600 | 500 | 400 | 300 | 200
Percent of User-specified Cooling Capacity, % | 145 | 100 | 90 | 80 | 70 | 60 | 50 | 40 | 30 | 20
Percent Full Load Cooling Capacity, % | 100 | 69.08 | 62.17 | 55.26 | 48.35 | 41.45 | 34.54 | 27.63 | 20.72 | 13.82
Percent of Full Load Power, % | 100 | 70.96 | 63.53 | 56.6 | 41.63 | 31.42 | 21.87 | 14.75 | 9.719 | 6.193
Unloading Sequence | Default | Default | Default | Default | Default | Default | Default | Default | Default | Default
Cooling Capacity, kW | 1 448 | 1 000. | 900 | 800 | 700 | 600 | 500 | 400 | 300 | 200
Heating Capacity, kW | 1 758 | 1 220. | 1 095 | 971.4 | 825.5 | 694.3 | 565.5 | 443.9 | 328.7 | 217.7
Total Unit Power, kW | 342.1 | 242.7 | 217.3 | 193.6 | 142.4 | 107.5 | 74.83 | 50.45 | 33.25 | 21.19
Nominal Unit Current Draw (RLA) | 522.49 | 369.9 | 332.7 | 297.9 | 222.3 | 168.4 | 117.3 | 79.1 | 52.1 | ---
Cooling Efficiency kW/kW | 4.232 | 4.12 | 4.141 | 4.132 | 4.916 | 5.583 | 6.682 | 7.929 | 9.024 | 9.44
Heating Efficiency, kW/kW | 5.139 | 5.027 | 5.04 | 5.017 | 5.797 | 6.46 | 7.558 | 8.799 | 9.888 | 10.28
A-Weighted Sound Pressure Level, dBA | 81 | 77 | 77 | 77 | 75 | 73 | 73 | 73 | 73 | -
Evaporator Data
Fluid Entering Temperature, °C | 13 | 13 | 13 | 13 | 13 | 12.86 | 11.72 | 10.57 | 9.43 | 8.29
Fluid Leaving Temperature, °C | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Fluid Flow Rate, L/s | 49.3 | 33.99 | 30.59 | 27.19 | 23.79 | 20.81 | 20.8 | 20.8 | 20.8 | 20.8
Pressure Drop, kPa | 29.9 | 15.2 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
Fouling Factor, (sqm-K)/kW | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018
Condenser Data
Fluid Entering Temperature, °C | 41 | 41 | 40 | 39 | 35 | 32 | 29 | 26 | 23 | 20
Fluid Leaving Temperature, °C | 49 | 49 | 47.23 | 45.42 | 40.47 | 36.61 | 32.76 | 28.95 | 25.19 | 21.45
Fluid Flow Rate, L/s | 57.82 | 40 | 39.96 | 39.93 | 39.85 | 39.78 | 39.73 | 39.67 | 39.61 | 39.54
Pressure Drop, kPa | 43.9 | 22.3 | 22.5 | 22.7 | 23.4 | 24 | 24.6 | 25.3 | 26.1 | 26.9
Fouling Factor, (sqm-K)/kW | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044
Note:
(**): Column displaying effective unit full load performances
(***): Column displays unit performance at the 'required capacity' and design conditions specified
(1) Compressor cycling is expected. Stated performances are average.
Note: Performance is at nominal voltage. Chiller may unload if job site voltage is lower than 400 volts.
Sound pressure level was determined in accordance with AHRI Standard 575. Sound pressure level is the free field sound data (the unit is placed in free field over a reflecting plane).
Outside the scope of AHRI Water-Cooled Water-Chilling and Heat Pump Water-Heating Packages Certification Program or not optionally certified, but is rated in accordance with AHRI Standard
550/590 (I-P) and AHRI Standard 551/591 (SI).
Packaged Chiller Builder China Export 3.49 Page 3 of 4

## Table 1
Detailed Performance Summary For R-134a_Qx_100to20_dTe_const_Tc_41to20C Project: 30XW_China 07.20.2026 Prepared By: Mikhail Terekhov 03:47
Load Line
Unit Performance | ** | *** | [7 empty] | -1
User-specified Cooling Capacity, kW |  | 1000 | 900 | 800 | 700 | 600 | 500 | 400 | 300 | 200
Percent of User-specified Cooling Capacity, % | 145 | 100 | 90 | 80 | 70 | 60 | 50 | 40 | 30 | 20
Percent Full Load Cooling Capacity, % | 100 | 69.08 | 62.17 | 55.26 | 48.35 | 41.45 | 34.54 | 27.63 | 20.72 | 13.82
Percent of Full Load Power, % | 100 | 70.96 | 63.53 | 56.6 | 41.63 | 31.42 | 21.87 | 14.75 | 9.719 | 6.193
Unloading Sequence | Default | Default | Default | Default | Default | Default | Default | Default | Default | Default
Cooling Capacity, kW | 1 448 | 1 000. | 900 | 800 | 700 | 600 | 500 | 400 | 300 | 200
Heating Capacity, kW | 1 758 | 1 220. | 1 095 | 971.4 | 825.5 | 694.3 | 565.5 | 443.9 | 328.7 | 217.7
Total Unit Power, kW | 342.1 | 242.7 | 217.3 | 193.6 | 142.4 | 107.5 | 74.83 | 50.45 | 33.25 | 21.19
Nominal Unit Current Draw (RLA) | 522.49 | 369.9 | 332.7 | 297.9 | 222.3 | 168.4 | 117.3 | 79.1 | 52.1 | ---
Cooling Efficiency kW/kW | 4.232 | 4.12 | 4.141 | 4.132 | 4.916 | 5.583 | 6.682 | 7.929 | 9.024 | 9.44
Heating Efficiency, kW/kW | 5.139 | 5.027 | 5.04 | 5.017 | 5.797 | 6.46 | 7.558 | 8.799 | 9.888 | 10.28
A-Weighted Sound Pressure Level, dBA | 81 | 77 | 77 | 77 | 75 | 73 | 73 | 73 | 73 | -
Evaporator Data
Fluid Entering Temperature, °C | 13 | 13 | 13 | 13 | 13 | 12.86 | 11.72 | 10.57 | 9.43 | 8.29
Fluid Leaving Temperature, °C | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Fluid Flow Rate, L/s | 49.3 | 33.99 | 30.59 | 27.19 | 23.79 | 20.81 | 20.8 | 20.8 | 20.8 | 20.8
Pressure Drop, kPa | 29.9 | 15.2 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
Fouling Factor, (sqm-K)/kW | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018
Condenser Data
Fluid Entering Temperature, °C | 41 | 41 | 40 | 39 | 35 | 32 | 29 | 26 | 23 | 20
Fluid Leaving Temperature, °C | 49 | 49 | 47.23 | 45.42 | 40.47 | 36.61 | 32.76 | 28.95 | 25.19 | 21.45
Fluid Flow Rate, L/s | 57.82 | 40 | 39.96 | 39.93 | 39.85 | 39.78 | 39.73 | 39.67 | 39.61 | 39.54
Pressure Drop, kPa | 43.9 | 22.3 | 22.5 | 22.7 | 23.4 | 24 | 24.6 | 25.3 | 26.1 | 26.9
Fouling Factor, (sqm-K)/kW | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044
Note:
(**): Column displaying effective unit full load performances
(***): Column displays unit performance at the 'required capacity' and design conditions specified
(1) Compressor cycling is expected. Stated performances are average.
Note: Performance is at nominal voltage. Chiller may unload if job site voltage is lower than 400 volts.
Sound pressure level was determined in accordance with AHRI Standard 575. Sound pressure level is the free field sound data (the unit is placed in free field over a reflecting plane).
Outside the scope of AHRI Water-Cooled Water-Chilling and Heat Pump Water-Heating Packages Certification Program or not optionally certified, but is rated in accordance with AHRI Standard
550/590 (I-P) and AHRI Standard 551/591 (SI).
Packaged Chiller Builder China Export 3.49 Page 3 of 4